## Sheet1
Sizing of Water Distribution Systems | [7 empty] | TOTAL FU | 0
Required Service Size NPS
Plumbing Fixture or Device | Minimum Nominal Pipe Size of Supply Pipe, NPS | Private Use Hydraulic Load fixture units |  |  | Public Use Hydraulic Load fixture units |  |  | Private Use Calculation Calculated on H/C Total
|  | Cold | Hot | Total | Cold | Hot | Total | Enter # of fixtures | Total FU
Bathroom group with 6 LPF flush tank |  | 2.7 | 1.5 | 3.6 |  |  |  |  | 0
Bathroom group with greater than 6 LPF flush tank |  | 4 | 3 | 6 |  |  |  |  | 0
Bathroom group with more than 3 plumbing fixtures | [8 empty] | 0
Bathtub with or without shower head | 1/2 | 1 | 1 | 1.4 | 3 | 3 | 4 |  | 0
Bathtub with NPS ¾ spout | 3/4 | 7.5 | 7.5 | 10 | 7.5 | 7.5 | 10 |  | 0
Bedpan washer | 1 |  |  |  | 7.5 | 7.5 | 10 |  | 0
Bidet | 3/8 | 1.5 | 1.5 | 2 |  |  |  |  | 0
Clothes washer, 3.5 kg | 1/2 | 1 | 1 | 1.4 | 2.25 | 2.25 | 3 |  | 0
Clothes washer, 6.8 kg | 1/2 |  |  |  | 3 | 3 | 4 |  | 0
Clothes washer, commercial | [8 empty] | 0
Dental lavatory | 3/8 |  |  |  | 1.5 | 1.5 | 2 |  | 0
Dental unit, cuspidor | 3/8 |  |  |  | 1 |  | 1 |  | 0
Dishwasher, commercial | [8 empty] | 0
Dishwasher, domestic | 3/8 |  | 1.4 | 1.4 |  |  |  |  | 0
Drinking fountain or water cooler | 3/8 |  |  |  | 0.25 |  | 0.25 |  | 0
Hose bibb | 1/2 | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 0
Hose bibb | 3/4 | 3 |  | 3 | 6 |  | 6 |  | 0
Hose bibb, combination hot and cold | 1/2 | 1.9 | 1.9 | 2.5 | 1.9 | 1.9 | 2.5 |  | 0
Lavatory, 8.3 LPM or less | 3/8 | 0.5 | 0.5 | 0.7 | 1.5 | 1.5 | 2 |  | 0
Lavatory, greater than 8.3 LPM | 3/8 | 0.75 | 0.75 | 1 | 1.5 | 1.5 | 2 |  | 0
Sink, bar | 3/8 | 0.75 | 0.75 | 1 | 1.5 | 1.5 | 2 |  | 0
Sink, clinic service faucet | 1/2 |  |  |  | 2.25 | 2.25 | 3 |  | 0
Sink, clinic service with direct flush valve | 1 |  |  |  | 6 |  | 6 |  | 0
Sink, kitchen commercial, per faucet | 1/2 |  |  |  | 3 | 3 | 4 |  | 0
Sink, kitchen domestic, 8.3 LPM | 3/8 | 1 | 1 | 1.4 | 1 | 1 | 1.4 |  | 0
Sink, kitchen domestic, greater than 8.3 LPM | 3/8 | 1.5 | 1.5 | 2 | 1.5 | 1.5 | 2 |  | 0
Sink, laboratory | 3/8 |  |  |  | 1.5 | 1.5 | 2 |  | 0
Sink, laundry (1 or 2 compartments) | 3/8 | 1 | 1 | 1.4 | 1 | 1 | 1.4 |  | 0
Sink, service or mop basin | 1/2 |  |  |  | 2.25 | 2.25 | 3 |  | 0
Sink, washup, per faucet | 1/2 |  |  |  | 1.5 | 1.5 | 2 |  | 0
Shower head, 9.5 LPM or less per head | 1/2 | 1 | 1 | 1.4 | 3 | 3 | 4 |  | 0
Shower head, greater than 9.5 LPM per head | 1/2 | 1.5 | 1.5 | 2 | 3 | 3 | 4 |  | 0
Shower, spray, multi-head, fixture units per head |  | 1 | 1 | 1.4 | 3 | 3 | 4 |  | 0
Urinal, with direct flush valve | 3/4 | [7 empty] | 0
Urinal, with flush tank | 3/8 | 3 |  | 3 | 3 |  | 3 |  | 0
Urinal, with self-closing metering valve | 1/2 | 2 |  | 2 | 4 |  | 4 |  | 0
Water closet, 6 LPF or less with flush tank | 3/8 | 2.2 |  | 2.2 | 2.2 |  | 2.2 |  | 0
Water closet, greater than 6 LPF with flush tank | 3/8 | 3 |  | 3 | 5 |  | 5 |  | 0
Water closet, with direct flush valve | 1 | [7 empty] | 0
Simple Water Service Sizing
Required Nominal Pipe Size of Water Pipe, NPS | Water Velocity, m/s
| 3 | 2.4 | 1.5 |  |  |  |  | 0
Hydraulic Load, fixture units
1/2" | 8 | 7 | 4
3/4" | 21 | 16 | 9
1" | 43 | 31 | 18
1-1/4" | 83 | 57 | 30